## Slide 1: Why We Do Surveys
2024 UF TREEO Conference
Presented By: Steve Fox, SC DHEC

## Slide 2
Large Hospitals/Clinics
Hangar's w/Fabrication Equipment
Warehouses
Construction/Facility Maint. Shops
Laboratory Buildings
Dental Facilities
Munition Storage ( Nuclear & Non-Nuclear Storage)
Auto Centers
Fuel Farms
Types of Facilities Connected
Office/Administration Support
Fitness Centers/Ball Fields
Fire Dept
Water Plant/Wastewater Plant
Fire System Distribution Facilities
Dining Facilities/cafeteria
Retail Stores/Grocery/Food Court
Dry Cleaners
Dormitories
Medical Examiner/Mortuary Affaires
Basically, a Small City

## Slide 3
How do we get Flo??
We Need a DIFFERNCE in PRESSURE
Flow
Pressure??
Partial Credit
Notes: The 2 types of backflow are: BACKSIPHONAGE & BACKPRESSURE

## Slide 4
What do we need to create flow??
We need a Pathway/Link and a difference in Pressure
50 psi
30 psi
High pressure always goes to low pressure
Notes: The 2 types of backflow are: BACKSIPHONAGE & BACKPRESSURE

## Slide 5
What happens when we have a Backflow Event???

## Slide 6
QUICK REVIEW –
Codes, Regulations, Standards used for survey

## Slide 7: Survey Preparation/Considerations
Codes and Regulations – Must know relevant codes. This case study was under IPC & UPC…
Containment vs. Isolation? or a combination
Field Forms/Data Entry Process (i.e., how will you document field data?)
Ladders, equipment (considerations for inspecting pipe above tile)!

## Slide 8: Survey Preparation/Considerations
5. Site Water Main and Architectural Drawings – Showing All Areas, plumbing drawings, etc.
Meet with Personnel Familiar w/ Water Systems
PPE (eye protection, hearing protection..etc.)
Clarify Accessibility ( entree, master keys, permission, escorts, Security Concerns, etc.)
Communication – Escorts, Facility Managers, Facility occupants

## Slide 9: Backflow Preventer–Selection Criteria
Evaluate Hazard Level of substance that could backflow – High/Health Hazard or Low Hazard/Non-health Hazard?
Could backflow occur due to Backpressure, Backsiphonage, or BOTH?
Is “Continuous Pressure” resulting from a downstream shutoff/control valve possible (Y/N)?
Notes: When selecting the correct backflow preventer to control a cross connection, there are 3 main questions to review. By answering these 3 questions, the proper selection of the appropriate backflow preventer can be obtained for any cross connection. These questions will be reviewed in more detail throughout this training course.

## Slide 10: FACILITY CONTAINMENT EVALUATION
RPBP
City Water Flow
Unprotected Bypass

## Slide 11: Service Connection/Medical Examiners

## Slide 12: Fast Food Service Connection.. Is this correct?

## Slide 13: Fire Service Connection

## Slide 14: Fire Service Connection, Is this Correct??

## Slide 15: CROSS CONNECTION SURVEY ISOLATION EVALUATION

## Slide 16: Hose Bibbs/Faucets

## Slide 17: Internal: Autopsy/Embalming Station Supply
RPBP in main supply

## Slide 18
Wye Connection with
Shut-off Valves
Potable Water Supply
Janitor Closet
Connection to Chemicals w/Valves downstream of AVB & Backpressure from elivation

## Slide 19
Correct Device??
Janitor Closet

## Slide 20: Fire Dept. Hose Reel & Fill Station

## Slide 21: Chiller/Boiler Make-up

## Slide 22: Chiller/Boiler Make-up

## Slide 23: Other Cooling Systems
“Liebert Units” - filled cooling system. Coolant is circulated elsewhere to an air-cooled heat exchanger or chiller unit.
Small water line may enter Liebert Unit to minimize static electricity/arching that could damage sensitive equipment. Air gap required in supply to discharge tray – controlled by solenoid valve.

## Slide 24: Liebert Unit Supply…

## Slide 25: Dental Clinic Exam/Lab Room Supply
Could use some labeling

## Slide 26: Sinks/Spray Stations

## Slide 27: “Macerator”
Disposal of bedpan pulp materials and waste
Machine pulverizes materials with addition of water to facilitate decomposition and drainage
Water typically flows from top of lid
RPBP may be recommended – water supply is typically threaded hose connection from behind unit

## Slide 28: “SAF T” Pumps
Disposal of infectious liquid medical waste
Potable water flows through venturi – aspirating dangerous fluids to waste stream (High Hazard!)
Reduced pressure principle backflow prevention assembly
Commonly found - Operating Room areas
Must review drainage of RPBP

## Slide 29: Water Cooling Line-Lab Equipment
¼” Potable Water Supply to Lab Equipment for Cooling
¼” Potable Water From Lab Equipment to Drain-
No Air Gap
Notes: This photo shows a quarter inch potable water supply line flowing to a piece of lab equipment for cooling. Once the water line cools the equipment, it flows into the sewer drain and is directly connected as shown. There is no air gap on the drain. If the potable water supply experiences a vacuum, water from the sewer drain may backsiphon into the water supply. An air gap must be fabricated to control the cross connection.

## Slide 30: RO/Deionized/Softener Water Systems

## Slide 31: Autoclave/Sterilizer Processing

## Slide 32: Hose Reels

## Slide 33: Cutting Machine
High or Low Hazard? High
Backsiphonage and/or Backpressure? Backsiphonage
Continuous Pressure? Yes
Protect Supply with SVB,PVB, or RPBP!
Potable Water Supply
Water Discharge
Notes: This photo shows a quarter inch potable water supply line flowing to a piece of lab equipment for cooling. Once the water line cools the equipment, it flows into the sewer drain and is directly connected as shown. There is no air gap on the drain. If the potable water supply experiences a vacuum, water from the sewer drain may back-siphon into the water supply. An air gap must be fabricated to control the cross connection.

## Slide 34
Dishwasher AVB
Soap Dispenser AVB
Hand Sprayer
Garbage Disposal AVB
Notes: What can you identify in this picture?
Dishwasher with AVB
  Things to look for:
    AVB at least 6” above down steam uses
    No valves down stream
    AVB installed in the vertical position
Soap Dispenser
    AVB at least 6” above down steam uses
    No valves down stream
    AVB installed in the vertical position
Hand Sprayer
  Remove hand sprayer from the hook and verify retention spring will maintain hand sprayer at least 1” above compartment sink flood level rim
Garbage Disposal
    AVB at least 6” above down steam uses
    AVB installed in the vertical position
    No valves down stream

## Slide 35: Pot Filler Hose With Valve – PVB/SVB

## Slide 36: Steamer & Combi-Style Ovens - VDCV
Used to reheat or warm food
May have both a hot and cold-water supply
May contain additives to feed water
Any steamer additives should be approved by USDA, FDA, or DOH
Subject to backpressure due to thermal expansion

## Slide 37: Trap Seal Primer Valves – Water Supply Fed

## Slide 38: Car Wash

## Slide 39: Decorative Fountains/Water Walls
High Hazard Cross-Connection!
Chemical treatment, exposure, bacterial growth, etc.
Many hospitals are decommissioning due to Legionella concerns…

## Slide 40: Decorative Fountains – Typical System Makeup

## Slide 41: Irrigation Supply
IPC Section 608 - Valves & outlets below grade: “ Potable outlets and combination stop & wastes valves SHALL NOT be installed underground or below grade.”
IPC Section 608 – Lawn Irrigation shall be protected using an AVB, PVB or RP…
They must consider this to be a High Hazard System

## Slide 42: Yard Hydrants…
“Potable water outlets and combination stop-and-waste valves shall not be installed underground or below grade. Freezeproof yard hydrants that drain the riser into the ground are consid­ered to be stop-and-waste valves.”
Exception: Freezeproof yard hydrants that drain the riser into the ground shall be permitted to be installed, provided that the potable water supply to such hydrants is protected upstream of the hydrants and the hydrants are permanently identified as non-potable outlets by approved signage that reads as follows: "Caution, Non-potable Water. Do Not Drink."

## Slide 43: Bulk Water Safety

## Slide 45: Report Out Information
Inventory of all backflow prevention assemblies, devices and methods
Itemized list of recommendations/requirements based upon survey information – be specific in terms of location, system, etc.
Service connection assessment
Internal Program Compliance, Local/State or OSHA Compliance
What do we have, and what do we need to do?

## Slide 46: Survey Recommendations/Tips
Ask Questions – How do you use this, or do you still use this? What does this hose supply?, etc.
Black Box Evaluation – Cross Connections:
  1. Where/how does the water go in?
  2. What does the water do when inside?
  3. Does water come out, and where/how?
Be an “educator”, not just an “enforcer”

## Slide 47: Survey Recommendations/Tips
Don’t Rush – Take your time, ask questions, attention to detail, be a detective
Know your Codes and Regulations:
  1. Have Plumbing Code readily available
  2. List of backflow preventer approvals
  3. Local ordinance, state reg’s, etc.
Always assume client does not know what you’re talking about – education is key

## Slide 49
QUESTIONS?
Steve Fox
SC DHEC
Cross-Connection Control Program Coordinator
2600 Bull Street
Columbia, SC 20201
(Office)803-898-4426
foxsc@dhec.sc.gov